## Load Schedule
LOAD SCHEDULE — D1-MDB-COM-FOH1A-A
DayOne CTP Building D ¦ Common Area Main Distribution Board
Board Designation: | D1-MDB-COM-FOH1A-A |  |  |  | Supply Source: | D1-SB-COM-FOH-BS1-A
Location: | Common Area / FOH |  |  |  | Incomer CB: | 160AT/160AF TPN MCCB, 36kA (L,S,I)
Busbar Rating: | 160A, 4P Insulated CU Busbar |  |  |  | Incomer Cable: | 4×1C 70mm² XLPE/LSZH CU + 1C 35mm² CU CPC
SECTION A — INCOMER
Circuit No. | Description / Load Name | CB Rating (A) | CB Type | No. of Poles | Breaking Cap. | Connected Load (kW) | Demand Factor | Max Demand (kW) | Current (A) | Cable Size | Cable Route | Remarks | Status
INCOMER | Supply from D1-SB-COM-FOH-BS1-A | 160A | MCCB (L,S,I) | 3P+N | 36kA | - | - | - | - | 4×1C 70mm² XLPE/LSZH CU +1C 35mm² CU CPC | Cable Ladder / Tray | 160AT/160AF | ACTIVE
SECTION B — OUTGOING CIRCUITS (FEEDERS TO SUB-BOARDS)
Circuit No. | Description / Load Name | CB Rating (A) | CB Type | No. of Poles | Breaking Cap. | Connected Load (kW) | Demand Factor | Max Demand (kW) | Current (A) | Cable Size | Cable Route | Remarks | Status
P-1RYB | D1-DB-MMR3S1B-A (MMR / Server Room Sub-Board) | 63A | MCCB | 3P+N | 36kA |  |  |  |  | 4×1C 16mm² LSZH CU +1C 16mm² CU CPC | Cable Trunking / Conduit |  | ACTIVE
2RYB | D1-DB-COM-FOH1A-A (Common Area / FOH Sub-Distribution Board) | 63A | MCCB | 3P+N | 36kA |  |  |  |  | 4×1C 16mm² LSZH CU +1C 16mm² CU CPC | Cable Trunking / Conduit |  | ACTIVE
3RYB | SPARE | 63A | MCCB | 3P+N | 36kA | - | - | - | - | - | - | Spare Way | SPARE
4RYB | SPARE | 63A | MCCB | 3P+N | 36kA | - | - | - | - | - | - | Spare Way | SPARE
5RYB | SPARE | 63A | MCCB | 3P+N | 36kA | - | - | - | - | - | - | Spare Way | SPARE
6RYB | SPARE | 63A | MCCB | 3P+N | 36kA | - | - | - | - | - | - | Spare Way | SPARE
7RYB | SPARE | 63A | MCCB | 3P+N | 36kA | - | - | - | - | - | - | Spare Way | SPARE
8RYB | SPARE | 63A | MCCB | 3P+N | 36kA | - | - | - | - | - | - | Spare Way | SPARE
SECTION C — PANEL ACCESSORIES & METERING
Item | Description | Standard / Spec | Qty | Remarks
1 | Surge Protection Device (SPD) | Type 2, In≥40kA, IEC 61643 | 1 set | 8/20µs, with 6A MCB
2 | Earth Leakage Relay (ELR) | — | 1 no. | Connected to ZCT
3 | Zero Core Current Transformer (ZCT) | — | 1 no.
4 | Power Meter (PM) | Class 0.5, BMS output | 1 no. | Connected to BMS
5 | BMS Interface / Transducer | Class 0.5 | 1 set
6 | 160A 4P Insulated CU Busbar | 160A rated, 4 pole | 1 set
NOTES
1. Board designation: D1-MDB-COM-FOH1A-A — FOR COMMON AREA (1 NO.)
2. Incomer supply from D1-SB-COM-FOH-BS1-A via 4×1C 70mm² XLPE/LSZH CU + 1C 35mm² CU CPC on cable ladder/tray.
3. All outgoing circuits rated 63A TPN MCCB 36kA. Feeder cables: 4×1C 16mm² LSZH CU + 1C 16mm² CU CPC on cable trunking/conduit.
4. FS = Fuse Switch; ST = Isolator Switch (shown on drawing per circuit).
5. Installed capacity (kW) and demand factor to be populated by M&E Engineer when load data is available.
6. ⚠️ QUERY RECOMMENDED: Room/Equipment names and installed capacity (kW) not embedded in DXF — confirm with panel schedule or M&E Engineer.
7. Drawing ref: D1-MDB-COM-FOH1A-A (DXF schematic). Verify against issued IFC drawings before pricing.