## D1-DB-COM-FOHRA-A
LOAD SCHEDULE – D1-DB-COM-FOHRA-A
FOR | FOR FOH ROOM LIGHTING, EMERGENCY LIGHTING, POWER POINT AND AC POINT
FROM | FROM D1-MDB-COM-FOHRA-A
INCOMER CB | 63A TPN MCCB,36KA
BUSBAR | 63A RATED 4P INSULATED CU BUSBAR
FEED CABLE | 4 x 1C 16mm² LSZH CU + 1C 16mm² CU CPC ON CABLE TRUNKING / CONDUIT
CIRCUIT NO. | DESCRIPTION | INSTALLED CAPACITY (kW) | CB RATING | CABLE SIZE
GROUP LT — 40A 4P RCCB (100mA)
LT-1R | FOR LIGHTING WITH TIMER | 0.54 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-1Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.63 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-1B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.36 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-2R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.54 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-2Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.54 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-2B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.63 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-3R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.54 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-3Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.63 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-3B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.81 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-4R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.72 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-4Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.81 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-4B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.54 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-5R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.36 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-5Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.36 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
LT-5B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS |  | 10A SPN MCB 10KA
LT-6R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS |  | 10A SPN MCB 10KA
GROUP L1 — 40A 4P RCCB (100mA)
L1-1R | FOR LIGHTING | 0.48 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-1Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.39 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-1B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.27 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-2R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.18 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-2Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.18 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-2B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.18 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-3R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.28 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-3Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.28 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-3B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.06 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-4R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.06 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L1-4Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS |  | 10A SPN MCB 10KA
L1-4B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS |  | 10A SPN MCB 10KA
GROUP L2 — 40A 4P RCCB (100mA)
L2-1R | FOR EMERGENCY LIGHTING | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-1Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-1B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-2R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-2Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-2B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-3R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-3Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-3B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-4R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-4Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.5 | 10A SPN MCB 10KA | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
L2-4B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS |  | 10A SPN MCB 10KA
GROUP P — 40A 4P RCCB (100mA)
P-1R | GENERAL SSOs | 1.2 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
P-1Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 1.2 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
P-1B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 1.2 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
P-2R | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 1.2 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
P-2Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 1.2 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
P-2B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 1.2 | 20A SPN MCB 10KA
GROUP AC — 40A 4P RCCB (100mA)
AC-1R | FOR POWER EQUIPMENT AC / 2P,16A ISOLATOR FOR FCU/EAF | 2.5 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
AC-1Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 2.5 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
AC-1B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.25 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
AC-2R | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 0.25 | 20A SPN MCB 10KA | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS
AC-2Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS |  | 20A SPN MCB 10KA
AC-2B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS |  | 20A SPN MCB 10KA