## D1-DB-COM-FOHRA-A
LOAD SCHEDULE — D1-DB-COM-FOHRA-A
DayOne CTP Building D ¦ FOR FOH ROOM LIGHTING, EMERGENCY LIGHTING, POWER POINT AND AC POINT
Board Designation: | D1-DB-COM-FOHRA-A |  |  |  | Supply Source: | FROM D1-MDB-COM-FOHRA-A
Location: | See Board Schedule |  |  |  | Incomer CB: | 63A 3P+N MCCB (L,S,I), 36kA
Busbar Rating: | 63A RATED 4P INSULATED CU BUSBAR |  |  |  | Incomer Cable: | 4 x 1C 16mm² LSZH CU + 1C 16mm² CU CPC
SECTION A — INCOMER
Circuit No. | Description / Load Name | CB Rating (A) | CB Type | No. of Poles | Breaking Cap. | Connected Load (kW) | Demand Factor | Max Demand (kW) | Current (A) | Cable Size | Cable Route | Remarks | Status
INCOMER | FROM D1-MDB-COM-FOHRA-A | 63A | MCCB (L,S,I) | 3P+N | 36kA |  |  |  |  | 4 x 1C 16mm² LSZH CU + 1C 16mm² CU CPC | Cable Trunking / Conduit |  | ACTIVE
SECTION B — OUTGOING CIRCUITS
Circuit No. | Description / Load Name | CB Rating (A) | CB Type | No. of Poles | Breaking Cap. | Connected Load (kW) | Demand Factor | Max Demand (kW) | Current (A) | Cable Size | Cable Route | Remarks | Status
GROUP LT ¦ 40A 4P+N RCCB — FOR LIGHTING WITH TIMER
LT-1R | FOR LIGHTING WITH TIMER | 10A | MCB | 1P | 10kA | 0.54 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-1Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.63 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-1B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.36 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-2R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.54 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-2Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.54 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-2B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.63 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-3R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.54 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-3Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.63 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-3B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.81 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-4R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.72 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-4Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.81 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-4B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.54 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-5R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.36 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-5Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.36 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
LT-5B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | [7 empty] | ACTIVE
LT-6R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | [7 empty] | ACTIVE
GROUP L1 ¦ 40A 4P+N RCCB — FOR LIGHTING
L1-1R | FOR LIGHTING | 10A | MCB | 1P | 10kA | 0.48 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-1Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.39 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-1B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.27 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-2R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.18 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-2Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.18 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-2B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.18 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-3R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.28 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-3Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.28 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-3B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.06 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-4R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.06 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L1-4Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | [7 empty] | ACTIVE
L1-4B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | [7 empty] | ACTIVE
GROUP L2 ¦ 40A 4P+N RCCB — FOR EMERGENCY LIGHTING
L2-1R | FOR EMERGENCY LIGHTING | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-1Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-1B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-2R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-2Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-2B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-3R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-3Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-3B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-4R | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-4Y | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | 0.5 |  |  |  | 2x1C 2.5mm² + 2.5mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
L2-4B | 2x1C 2.5mm2^ + 2.5mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 10A | MCB | 1P | 10kA | [7 empty] | ACTIVE
GROUP P ¦ 40A 4P+N RCCB — GENERAL SSOs
P-1R | GENERAL SSOs | 20A | MCB | 1P | 10kA | 1.2 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
P-1Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 1.2 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
P-1B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 1.2 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
P-2R | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 1.2 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
P-2Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 1.2 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
P-2B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 1.2 | [6 empty] | ACTIVE
GROUP AC ¦ 40A 4P+N RCCB — FOR POWER EQUIPMENT AC / 2P,16A ISOLATOR FOR FCU/EAF
AC-1R | FOR POWER EQUIPMENT AC / 2P,16A ISOLATOR FOR FCU/EAF | 20A | MCB | 1P | 10kA | 2.5 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
AC-1Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 2.5 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
AC-1B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 0.25 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
AC-2R | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | 0.25 |  |  |  | 2x1C 4.0mm² + 4.0mm² CPC LSZH | Cable Trunking/Conduits |  | ACTIVE
AC-2Y | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | [7 empty] | ACTIVE
AC-2B | 2x1C 4.0mm2^ + 4.0mm2^ CPC LSZH ON CABLE TRUNKING/CONDUITS | 20A | MCB | 1P | 10kA | [7 empty] | ACTIVE
SECTION C — PANEL ACCESSORIES & METERING
Item | Description | Standard / Spec | Qty | Remarks
SPD | Surge Protection Device (SPD) | 8/20µS TYPE 2, In≥20KA ACCORDING TO IEC61643 | 1 set | with 6A MCB
PM | Power Meter (PM) | CLASS 0.5 | 1 no. | BMS output
BMS | BMS Interface / Transducer | CLASS 0.5 | 1 set
LT | Lighting Control Timer / Sensor | LIGHITNG CONTROL TIMER / SENSOR | 1 set
BUS | Insulated CU Busbar | 63A RATED 4P INSULATED CU BUSBAR | 1 set
NOTES
1. Board designation: D1-DB-COM-FOHRA-A
2. Incomer supply FROM D1-MDB-COM-FOHRA-A via 4 x 1C 16mm² LSZH CU + 1C 16mm² CU CPC on Cable Trunking / Conduit.
3. Incomer CB: 63A 3P+N MCCB (L,S,I), 36kA.
4. Installed capacity (kW) and demand factor to be verified by M&E Engineer.
5. ⚠️ QUERY RECOMMENDED: Confirm kW values and circuit descriptions against issued IFC drawings.
6. Drawing ref: D1-DB-COM-FOHRA-A (DXF schematic). Verify before pricing.